## IEC62559-2
1 Description of the use case | Instructions are provided as comments in the rows
1.1 Name of use case
Use case identification
| ID | UC1
| Area/ Domain(s)/ Zone(s) | Area: Energy system Domain: Transmission, DER, Customer Premises Zones: Operation, Market
| Name of use case | Frequency control
1.2 Version management
| Version No. | 1.0
| Date | 2021-10-31
| Name of author(s) | Andraž Andolšek (cyberGRID), Christoph Gutschi (cyberGRID), Marjolaine Farré (Trialog), Elchaysse Soudjae (Electricité de Mayotte)
| Changes | First version
| Approval status | Final
1.3 Scope and objectives of use case
| Scope | The scope of this use case is to examine the use of flexibility to restore system frequency to its nominal value of 50 Hz.
| Objective(s) | The main objective of this use case is to stabilize the electricity grid of the islands by establishing balancing services. Implementing the balancing services framework will help system operators to maintain the equilibrium between consumption and generation while minimizing the frequency deviation from the nominal values.
| Related business case(s) | /
1.4 Narrative of use case
| Short description | This high-level use case describes different scenarios incl. all required steps for the implementation of a tender based frequency control system. The UC differentiates between FCR (frequency containment reserve) and FRR (frequency restoration reserve) services. The explained approach is technology agnostic and supports any kind of flexibility resource, that can meet the technical requirements for balancing service provision. A common approach to handle different technologies for flexibility provision (industrial demand response, residential demand response aggregated by a VPP, smart charging of electric vehicles, aggregation of renewables (PV) via a VPP, battery energy storage, power-to-hydrogen electrolyser) is explained. The scope of the use case includes dimensioning of balancing service reserves for an islanding system, prequalification of suitable distributed energy assets and intermediary platforms (Virtual Power Plants, VPPs), tendering and contracting balancing services, balancing service activation, monitoring, validation, and remuneration. All periodic communication between the system operator and the market participants, like bidding, monitoring and activation is organized via a Flexibility Management and Trading Platform (FMTP). The use case focuses on the situation on the Island of Mayotte and aims to adapt to the historically grown infrastructure and processes, but also takes into account updates of the system operators SCADA in the near future.
| Complete description | Introduction to balancing services for frequency control The system operator Electricité de Mayotte (EDM), responsible for grid operation and supply of electric energy, needs to maintain the network frequency within a narrow bandwidth (+300 / -200 mHz) around 50 Hz. Frequency deviation is a consequence of an imbalance between generation (feed-in to the grid) and consumption (extraction from the grid) including losses of the grid itself. These imbalances are mainly caused by unpredictable fluctuations of the load (low impact on the grid frequency), general imprecisions in the load forecasting that cause improper generation schedules (medium impact) or rare fault-induced disconnection of entire branches or substations or even unexpected loss of generation (high impact). Until now, the electricity system in Mayotte relied on fast adaption of the generation of spinning diesel engines to balance the load fluctuations. These diesel engines also cover for the main generation schedule. The mechanisms to maintain the grid frequency within a narrow bandwidth can be distinguished between three main types of control, as shown in Figure 24. After an incident like the unexpected outage of a generator, the imbalance between load and generation causes an immediate decrease of the grid frequency, which is mainly limited by the kinetic energy stored in spinning machines (synchronous inertia). The higher the inertia of the rotating machines connected to the grid, the lower the gradient of frequency change (Df/Dt), also known as rate of change in frequency (ROCOF). The frequency stabilization by inertia is a physical effect, responding spontaneously to any frequency gradient and acting in both directions. New generations of inverters can provide a frequency gradient dependent feed-in (with only a minor time lag), which can be considered as “virtual inertia”. [See figure "Overview of phases of frequency control after a major outage" below] The frequency containment reserve (FCR), also known as primary control, provides a variable feed-in linearly depending on the deviation of the frequency (Df) from the target value of 50 Hz. FCR is required to act very fast. The required full activation time (FAT) is determined by the considered maximum imbalance (e.g., due to loss of the largest generation unit in the system), the maximum allowed frequency deviation and the typical inertia of the system. FCR is a very fast service that requires frequency measurements and control logic directly at the providing asset, usually a generator or battery. Some loads controlled by power electronics might also be feasible to provide FCR. Usually, FCR is a symmetric service that acts in both directions. The linear function of FCR power only depending on the frequency deviation enables a fast response to limit the frequency deviation but does not allow to bring the frequency back to the target value. Some transmission system operators (TSO), e.g., in the NORDPOOL, differentiate between Frequency Containment Reserve for Normal Operation (FCR-N) and Frequency Containment Reserve for Disturbances (FCR-D). FCR-N is a symmetric service providing upregulation and downregulation with a linear characteristic while FCR-D differentiate between upward (increase feed-in or decrease consumption) and downward (decrease feed-in or increase consumption) regulation. FCR-D is only activated after exceeding a threshold value of frequency deviation. [See figure "FCR architecture overview" below] The frequency restoration reserve FRR is managed by the system operator (SO) using the automatic generation control (AGC). The AGC calculates setpoints for multiple balancing providing assets (generators, batteries but also fast and precisely controllable loads like electrolyser). After reception of the setpoint the assets will adapt the power output within a defined FAT that may be longer than required for FCR. The AGC aims to bring the system frequency back to the target value. FRR requires reliable communication between the central AGC and the distributed assets. FRR can be divided into positive products for upward control and negative products for downward control. European TSO differentiate between faster, automatically controlled reserves (aFRR), that follow to instantaneous setpoints, and slower reserves that might be manually controlled (mFRR) and follow to received schedules. [See figure "FRR architecture overview" below] FCR and FRR provision in Europe usually require active power measurements with high precision (e.g., 0.5% error class) and submission of data points to the SO in short intervals (e.g., 1-2 s) for the purpose of real-time monitoring of provision and ex-post validation of the provided services. Additional Emergency measures will be activated in case that the frequency regulation system failed, and the frequency deviation exceeds defined thresholds. Emergency measure can include load shedding, disconnection of large, robust consumers or disconnection of generators. The rules for frequency protection devices to disconnect sensible assets in case of high frequency deviations must be defined accordingly to support system frequency stabilization and to avoid negative feedback on the frequency control mechanisms. Context The rising number of PV power plants to be installed and connected to the main grid in Mayotte may increase the difficulty of frequency control as the production is highly dependent on weather conditions challenging to forecast (e.g., a passing cloud leads to a decline in PV production) which may increase the imbalances between generation and consumption. With increasing number of PV generation, partly replacing diesel generators the ratio of spinning machines in the system will be reduced which has negative impact on the synchronous inertia. To avoid reaching low frequency thresholds leading to load shedding (48.5 Hz, 48 Hz and 47.5 Hz), the French Energy Regulatory Commission (CRE) granted an exemption to EDM to operate the grid at a higher frequency. The current mean frequency value is thus of 50.15 Hz, higher than the 50 Hz stipulated in the EU Electricity Network code. The main balancing service to cope with the frequency deviation currently applied on the island of Mayotte is the “primary reserve” (covering FCR and FRR), which is estimated at 15% of the daily demand and mainly supported by the EDM diesel generation sets of Longoni and Badamiers. The generators are limited to operate at 80-85% of their maximal capacity. For the past few years, the primary reserve hadn’t exceeded 8 MW, but this will change soon with an expected rising demand and RES integration. To stabilize the frequency in the island and ease the penetration of renewable energy, the French Energy Regulatory Commission CRE launched a call for tender to install a battery for frequency control in July 2018. This 4 MW/2 MWh battery should be installed and be ready to operate in October 2021. Following this installation, the exemption (of higher system frequency) should disappear for the time-being. It is estimated that further investments will be needed to fulfil the requirements that are foreseen in the future. One of the goals when considering the frequency use case is to find a way for moving from the energy assets providing frequency services with the help of fossil fuel to assets using renewable energy sources (RES) and Battery Energy Storage Systems (BESS). To further reduce the primary reserve provided by the EDM’s diesel generation sets new sources for providing frequency regulation services are needed to have a direct impact on reduction of CO2 emissions. The main challenges when implementing the frequency control framework are related to the identification of sufficient assets from RES to reduce the required capacity of fossil fueled generators that are capable to provide similar reliable frequency services. The use case describes the interactions between the main actors and platforms but doesn’t discuss the details of the balancing products. The details of the designed balancing products will be defined Deliverable D4.1 Report detailing the energy market framework and specific product design details. For the MAESHA project, it has been decided to examine how different flexibility sources could support the frequency control on the island: •Industrial Demand Response Industry’s main purpose is manufacturing of goods or provision of other services. Some industrial assets are additionally able to provide a certain help to the system operator by adjusting their internal manufacturing process and thus increase or decrease the consumption for the time being (load shifting) and help minimizing the frequency deviation. Such industrial energy assets usually have some restrictions, such as limited duration of delivery (e.g., max 4 h), poor controllability (e.g., ON-OFF operation), or can provide such action only at a certain time of the day or year. Therefore, industrial demand response is not considered as a primary source for providing balancing services to the power grid, but they may serve as secondary source for additional support when other services are already fully activated (e.g., for emergency measures). • Residential Demand Response managed by a virtual power plant (VPP) Residential customers may have flexible loads that end-users do not necessarily need instantaneously to ensure their comfort, e.g., air-conditioning units and electric heating, but also dishwashers, washing machines, cloth dryers, etc. Optimally controlling the on/off times of these devices, considering local frequency deviations, can help in ensuring the frequency stability. Depending on the characteristics of the device, the activation time and activation duration differ. Heat pumps or air conditioning units can be used for frequency response, considering the heat storage capacity of the building or heat storage in a hot water tank. The activation duration depends upon the stored heat capacity in the building or the tank and the comfort requirements of the end-users. These units can be activated very fast (remote switch-off) but their availability is difficult to forecast. • Smart Charging of electric vehicles (EV) and vehicle to grid (V2G) Smart charging of EV can be a source of consumption flexibility and theoretically be used even for balancing services. The challenges for provision of FRR by an EV are linked to the prediction of the charging process’ time and duration as well as the limited hours per day, when EV charging can be used for load shifting. Nevertheless, the forecasting of consumption and flexibility becomes easier on a fleet of EVs, as such an aggregate of a higher number of EV’s can provide ancillary services reliably using a minor share of the predicted consumption. Load reduction in EV charging can be achieved by reducing the charging power (e.g., switch from 3-phase to 1-phase charging) of a certain number of vehicles. Advanced fleet management might also allow downward services by increasing the charging power during the requested period. Feed-in of energy stored in the EV’s batteries (V2G) will been investigated as another possibility of upward regulation by EVs but comes with practical drawbacks like possible reduction of battery lifetime and the need for bidirectional inverters. Due to the nature of the fleet management and lower frequency of data acquisition, EV charging will be preferably applied for mFRR than for aFRR or FCR like frequency services. • Virtual Power Plant (VPP) aggregating RES The variability of renewable energy sources, such as wind and solar, are causing continuous, small frequency deviations due to their hard to predict short-term dynamics and their lack of synchronous inertia to stabilize the frequency during disturbances. Lowering the output of PV plants (downward regulation) during high frequency periods can support frequency stabilization. If PVs are operated below their maximal inverter power, PV plants can inject additional power into the grid with different activation times, ranging from seconds to minutes during low frequency periods (upward regulation). The latter will result in a reduction of overall generation or require the installation of PV batteries. The activation duration depends on the amount of reserve kept for upward frequency response and will be the result of a cost-benefit analysis, where the outcome depends on the remuneration of the different frequency response products compared to the value of electric energy fed-in by PV. In the last years, much development effort has been made on virtual inertia provided by PV and wind power, which might become state-of-the-art within the next decades. • Battery Energy Storage System By supplying or absorbing power in response to deviations from the nominal frequency and imbalances between supply and demand, the rapid response of a BESS will provide a frequency stabilizing services. The fast response capability of BESS allows them to participate in all kinds of frequency response (e.g., FCR, FRR) or even a fast or enhanced frequency response markets (activation in less than 5 s). The BESS will also provide virtual inertia by modulating active power as a function of the ROCOF. The duration of the service provision will be determined by the SoC. BESS providing ancillary services will require an additional charge management to maintain the state of charge (SOC) within predefined limits (e.g., 30%<SOC<70%) in order to ensure the continuous availability of upward and downward regulation ability. Load management (consumption or feed-in) is based on schedules and should be communicated with the SO, e.g., via an intraday program. The BESS should be able to provide multiple balancing services and perform load management in parallel. • Power-to-Hydrogen system Proton Exchange Membrane (PEM) electrolysers have the capability of modifying their load rapidly with very high ramps rates (i.e., within seconds) and within a wide operational range up to the nominal power. This flexibility can be utilized for large range of frequency regulation (e.g., FCR, aFRR, mFRR). Despite the hydrogen storage capacity, there is no limit in the duration of the service as the service is provided by reducing/increasing the load of the electrolyser. These DER provide their flexibility to the SO via the FMTP, as indicated in Figure below. [See figure "Architecture overview for frequency control in MAESHA" below] Functions This Use Case relies on the following functions: • Asset contraction and technical preparation, incl. pre-qualification • Detection of frequency deviations • Evaluation of flexibility available from different assets or via intermediate platforms • Contracting balancing service products • Calculation of setpoints by the AGC of the SO • Flexibility activation through the Flexibility Management and Trading Platform (FMTP) • Monitoring of service provision • Settlement process to remunerate flexibility activation This Use Case supports a technology-agnostic approach for provision of balancing services by central or decentralized energy assets. In the MAESHA project, the following technologies are aimed to be investigated in the scope of the use case demonstration. Investigated technology options for provision of balancing services The following technology options to provision of balancing services are aimed to be supported by the use case: • Detection of frequency deviations, central by SO or decentral by the DER • Frequency regulation by industrial DR • Frequency regulation by residential DR via VPP • Frequency regulation by Smart charging/V2G • Frequency regulation by RES via VPP • Frequency regulation by BESS • Frequency regulation by P2H system
1.5 Key performance indicators (KPI)
| ID | 4.2
| Name | Frequency range before and after the project
| Description | From [49.6;50.6] to [49.8;50.3] Hz
| Reference to mentioned use case objectives | /
1.6 Use case conditions
| Assumptions | • Industrial prosumers will be interested in and capable of providing flexibility services to the grid • Residential prosumers will be interested in providing flexibility services to the grid • For residential DR: buildings equipped with heating boilers or air-conditioning units with adequate control system in place • At least one battery for frequency control will be connected to the grid and to the FMTP • Batteries should react upon a control signal to change their power output • EV charging stations will be connected to the grid and operating • The output of the PV plants can be controlled • The PV plants should react upon a control signal to change their power output • EDM can update the AGC to communicate FRR setpoints to distributed assets via the FMTP • All assets providing FCR must be equipped with on-site frequency measurement devices with high precision. • Secure and reliable communication channels supporting bidirectional communication between the distributed assets, intermediate platforms (VPPs, EV charging management), the FMTP and the AGC • Contracts between the assets and EDM to ensure legal security during the test period
| Prerequisites | • For Smart charging EV: EVs must be plugged to the EV charging stations to participate in frequency control • AGC, FMTP and intermediate platforms are available, functioning, integrated, and tested
1.7 Further information to the use case for classification/mapping
| Relation to other use cases | Linked to “Voltage control” UC (UC2) as potential conflicts within flexibility products could appear.
| Level of depth | High-level use case
| Prioritisation | Obligatory. This UC should be demonstrated under real-life conditions
| Generic, regional or national relation | Regional relation
| Nature of the use case | Technical and business UC
| Further keywords for classification | Balancing services, load-frequency control, demand response, flexibility, distributed energy resources (DER)
1.8 General remarks
| General remarks | /
2 Diagrams of use case
| Diagram name | SGAM Business layer of the frequency control use case-specific architecture | SGAM Function layer of the frequency control use case-specific architecture | Overview of phases of frequency control after a major outage | FCR achitecture overview | FRR achitecture overview | Architecture overview for frequency control in MAESHA
| Diagram type | Architecture | Architecture | Description | Description | Description | Architecture
| Diagram URI type | Image | Image | Image | Image | Image | Image
| Diagram URI value | BusinessLayer_FrequencyControlUC | FunctionLayer_FrequencyControlUC | FrequencyControlPhasesAfterMajorOutage | FCR_Architecture | FRR_Architecture | FrequencyControlArchi_OverviewMAESHA
3 Technical details
3.1 Actors
| Grouping | Business Actor | Logical actors | Assets | Devices
| Group description | Physical or legal person that has his own interests, defined as "Business Goals" | Technical entity that takes part in the execution of a use case. A logical actor can be mapped to a physical component
| Actor name | TSO | Flexibility provider | Residential prosumer | Industrial prosumer | SCADA | AGC | Intermediate platform | Small-scale virtual power plant | Large-scale virtual power plant | EV charging management platform | FMTP | Distributed Energy Resource (DER) | PV power plant | Battery | P2H system | Diesel generator | EV charging station | Frequency meter | Local controller (PLC) Active power meter | Public meter
| Actor type | Business actor | Business actor | Business actor | Business actor | Logical actor | Logical actor | Logical actor | Logical actor | Logical actor | Logical actor | Logical actor | Asset | Asset | Asset | Asset | Asset | Device | Device | Device | Device
| Actor description | Transmission System Operator | Generic presentation of the energy asset capable of providing flexibility on request (balancing service provider) | A residential party that consumers electricity (Flexibility Provider) | An industrial party that consumes electricity (Flexibility Provider) | Supervisory Control and Data Acquisition – a supervisory computerized system that gathers and processes data and applies operational controls for transmission side systems used to control dispersed assets | Automatic gain control. Process to determine the amount of power needed to bring back the frequency to the nominal values. | Platform that aggregates flexibility energy assets (virtual power plant, EV charging management platform) | This is a type of Intermediate platforms. Software platform that aggregates the flexibility of residential prosumers and PV power plants | This is a type of Intermediate platforms. Software platform that aggregates the flexibility of industrial energy assets and BESS | A platform that manages and aggregates the charging power of multiple EV charging stations | Flexibility Management and Trading Platform | Generic presentation of the energy asset providing flexibility | Renewable energy source able to provide flexibility of feed-in | Energy storage system capable of providing different services to the grid | System to convert electricity (optimally from RES) into hydrogen that can be stored to use it eventually for different purposes (feedstock, electricity production, fuel) | Synchronous generators |  | Frequency meter, to measure frequency on the entire power network | Calibrated power meter to continuously measure the active power exchange with the public grid. Installed at the DER and controlled via PLC | Calibrated utility meter for energy metering, providing data in the settlement interval (e.g., 30 min)
| Further information specific to this use case | Electricité de Mayotte
3.2 References
| Name | Operational guidelines from ENTSO-E | Operational guidelines from the French government | ENTSO-E Role model
| No. | Ref-1 | Ref-2 | Ref-3
| References type | Operational guidelines | Operational guidelines | Role model
| Reference | Operational Handbook P1-Policy 1: Load-Frequency Control and Performance | French standards about system operation | The Harmonized Role Model
| Status | Final | Final | Version 2020-01
| Impact on use case | Medium | High | Medium
| Originator/organisation | ENTSO-E | French government | ENTSO-E
| Link | https://eepublicdownloads.entsoe.eu/clean-documents/pre2015/publications/entsoe/Operation_Handbook/Policy_1_final.pdf | https://codes.droit.org/PDF/Code%20de%20l'%C3%A9nergie.pdf | https://www.entsoe.eu/digital/cim/role-models/#harmonised-electricity-role-model
4 Step by step analysis of use case | 4.1 Overview of scenarios
Scenario conditions
| No. | Sc1 | Sc2 | Sc3 | Sc4 | Sc5 | Sc6 | Sc7 | Sc8
| Scenario name | Frequency reserve requirements | Detection of the frequency issues - FCR | Detection of the frequency issues - FRR | Contracting balancing service products | Flexibility activation through local controller - FCR | Flexibility activation through the Flexibility Management and Trading Platform (FMTP) - FRR | Settlement process to remunerate flexibility activation | Frequency control by flexibility provider
| Scenario description | Calculating the amount of FCR and FRR needed | Detection of the frequency deviations locally on the site of the flexibility provider | Detection of the frequency deviations centrally in the SCADA | Contractual obligations between the SO (EDM) and the flexibility providers | Activation of the flexibility providers automatically using its local controller | Activation of the flexibility providers automatically using centralized platform - FMTP | Validation and settlement of the activation responses | The process of flexibility provision by the flexibility provider
| Primary actor | System Operator | Flexibility provider | System Operator, with the help of the AGC | System Operator | Flexibility provider | FMTP | SO | Flexibility provider
| Triggering event | Long-term planning (yearly activity) | Continuous activity | Continuous activity | Periodic tender (yearly, monthly, weekly and/or daily) | Frequency deviation is detected on-site | Frequency deviation is detected by AGC | Daily or monthly | Reception of activation signal or activation schedule
| Pre-condition | Need for: - Historic data about electricity system - Mid-term consumption forecasts - List of planned new DER installations | Need for high precision frequency meter | Need for high precision frequency meter | Prequalified DER are available | FCR control algorithms are implemented in on-site controller | AGC’s control algorithms are trained with system characteristics | Meter data are available | Flexibility bid is accepted via FMTP
| Postcondition | Required amount of Inertia, FCR, FRR to be contracted and reserved are defined | Frequency deviations are detected on-site | Frequency deviations are detected by central AGC | List of available flexible capacity and price (merit order) is available | FCR provision by DER | FRR provision by DER | Remuneration of ancillary service provision per DER | Successful provision of flexibility service
4.2 Steps – Scenarios
| Scenario name: | Sc1 - Frequency reserve requirements | Sc1 - Frequency reserve requirements | Sc1 - Frequency reserve requirements | Sc1 - Frequency reserve requirements | Sc1 - Frequency reserve requirements | Sc1 - Frequency reserve requirements | Sc2 - Detection of the frequency issues - Frequency Containment Reservce (FCR) | Sc2 - Detection of the frequency issues - Frequency Containment Reservce (FCR) | Sc2 - Detection of the frequency issues - Frequency Containment Reservce (FCR) | Sc3 - Detection of the frequency issues - Frequency Restoration Reserve (FRR) | Sc3 - Detection of the frequency issues - Frequency Restoration Reserve (FRR) | Sc3 - Detection of the frequency issues - Frequency Restoration Reserve (FRR) | Sc3 - Detection of the frequency issues - Frequency Restoration Reserve (FRR) | Sc3 - Detection of the frequency issues - Frequency Restoration Reserve (FRR) | Sc4 - Contracting balancing service products | Sc4 - Contracting balancing service products | Sc4 - Contracting balancing service products | Sc4 - Contracting balancing service products | Sc4 - Contracting balancing service products | Sc4 - Contracting balancing service products | Sc4 - Contracting balancing service products | Sc5 - Flexibility activation through local controller - FCR | Sc5 - Flexibility activation through local controller - FCR | Sc5 - Flexibility activation through local controller - FCR | Sc5 - Flexibility activation through local controller - FCR | Sc5 - Flexibility activation through local controller - FCR | Sc5 - Flexibility activation through local controller - FCR | Sc5 - Flexibility activation through local controller - FCR | Sc6 - Flexibility activation through the Flexibility Management and Trading Platform - FRR | Sc6 - Flexibility activation through the Flexibility Management and Trading Platform - FRR | Sc6 - Flexibility activation through the Flexibility Management and Trading Platform - FRR | Sc6 - Flexibility activation through the Flexibility Management and Trading Platform - FRR | Sc6 - Flexibility activation through the Flexibility Management and Trading Platform - FRR | Sc6 - Flexibility activation through the Flexibility Management and Trading Platform - FRR | Sc6 - Flexibility activation through the Flexibility Management and Trading Platform - FRR | Sc6 - Flexibility activation through the Flexibility Management and Trading Platform - FRR | Sc6 - Flexibility activation through the Flexibility Management and Trading Platform - FRR | Sc6 - Flexibility activation through the Flexibility Management and Trading Platform - FRR | Sc6 - Flexibility activation through the Flexibility Management and Trading Platform - FRR | Sc6 - Flexibility activation through the Flexibility Management and Trading Platform - FRR | Sc6 - Flexibility activation through the Flexibility Management and Trading Platform - FRR | Sc7-Settlement process to remunerate flexibility activation | Sc7-Settlement process to remunerate flexibility activation | Sc7-Settlement process to remunerate flexibility activation | Sc8-Frequency control by flexibility provider | Sc8-Frequency control by flexibility provider | Sc8-Frequency control by flexibility provider | Sc8-Frequency control by flexibility provider | Sc8-Frequency control by flexibility provider | Sc8-Frequency control by flexibility provider | Sc8-Frequency control by flexibility provider | Sc8-Frequency control by flexibility provider | Sc8-Frequency control by flexibility provider | Sc8-Frequency control by flexibility provider | Sc8-Frequency control by flexibility provider | Sc8-Frequency control by flexibility provider | Sc8-Frequency control by flexibility provider
| Step No. | St1 | St2 | St3 | St4 | St5 | St6 | St1 | St2 | St3 | St1 | St2 | St3 | St4 | St5 | St1 | St2 | St3 | St4 | St5 | St6 | St7 | St1 | St2 | St3 | St4 | St5 | St6 | St7 | St1 | St2 | St3a | St3b | St4 | St5 | St6 | St7 | St8 | St9a | St9b | St10 | St11 | St1 | St2 | St3 | St1 | St2 | St3 | St4 | St5 | St6 | St7 | St8 | St9 | St10 | St11 | St12 | St13
| Event | Periodically (yearly) | Periodically (yearly) | Periodically (yearly) | Periodically (yearly) | Periodically (yearly) | St5 finished | Periodically (interval of 1s of faster) | New frequency measurement available | When freq. measurements arrive to the local controller | Continuously | Continuously | Frequency measurement received by AGC | Frequency measurement received by AGC | Frequency deviation calculated | After definition of technical require-ments | After reception of balancing service rules | After reception of tender announcement | SO received request for prequalification | Periodically (yearly, monthly, weekly, or daily) | St5 finalized | SO received bid for balancing service provision | Reception of FCR bid acceptance | FCR provision enabled | FCR setpoint calculated (continuously, e.g., 1s interval) | Continuously (e.g., 1s interval) | Continuously | FCR malperformance detected | FCR validation report received | Reception of FRR bid acceptance | New FRR setpoint available | Central assets’ FRR setpoint updated | Decentral assets’ FRR setpoint updated | FMTP received a new FRR setpoint | Intermediate platform receives activation request | DER received the activation request | Continuously (e.g., in 2s interval) | Continuously (e.g., in 2s interval) | Continuously | Yearly | FRR malperformance detected | FRR validation report received | Daily | After completing previous step | Monthly | Daily | Previous step finalized | Previous step finalized | Bid acceptance message received | Flexibility reservation request received | Continuously | Continuously | Activation setpoint received by DER | Continuously | New activation setpoint received by DER | Continuously | Activation end received by DER | Continuously (e.g., 2s interval)
| Name of process/activity | Define desired conditions for grid frequency | Collect data of the power system | Mid-term & long-term forecasts | Define design scenarios | Calculate the required amount of flexibility- balancing reserve needed on the island - FRR | Define balancing service products | Measure the network frequency | Submit the measured frequency to the local controller | Calculate frequency deviation | Measure grid frequency | Receive frequency measurement | Measured frequency is stored and available for processing | Calculate the frequency deviation | Calculate the new FRR setpoint | Publish technical and market rules for balancing services | Flexibility providers prepare for participation in balancing services | Aggregators prepare for participation in balancing services | Prequalify flexibility provider | Publish tender for balancing services | Submit balancing services bids | Contract balancing services | Enable FCR service | Calculate FCR setpoint | Follow new FCR setpoint | Send monitoring data to FMTP | Validate FCR provision | Inform flexibility provider about malperformance | Remedy FCR malperformance | Enable FRR service | Dispatch balancing assets | Receive new FRR setpoints | Receive new FRR setpoints | FMTP dispatches contracted flexibility providers | Intermediate platform distributes activation requests | FRR provision by DER | Send monitoring data to intermediate platform | Send monitoring data to AGC | Validate FRR provision | Validate FRR provision | Inform flexibility provider about malperformance | Remedy FRR malperformance | Process monitoring data | Accounting of balancing service provision | Remuneration of flexibility service provision | Forecast flexible capacity for upcoming tender period | Aggregator receives flexibility forecast | Participation in balancing service tender | Flexibility reservation request | Flexibility reservation | Real-time flexibility calculation | Listen to incoming setpoints | Start activation program | Listen to incoming setpoints | Change activation program | Listen to incoming setpoints | End activation program | Send monitoring data
| Description of process/activity | In a phase of mid-term planning, the SO defines the frequency control strategy, incl. nominal (target) frequency value, frequency bandwidth for operation and frequency thresholds for emergency actions | Collect the data to describe the power system (system model), historic measurements (load, frequency) and events (fault statistics) | The SO generates mid-term and long-term forecasts of the development of consumption and generation | The SO identifies critical situations (e.g., yearly peak load, separation of parts of the grid, etc.) and defines design scenarios comprising all possible critical situations. | The SO assesses the amount of flexibility (FCR, FRR balancing reserve) required to perform the load-frequency control of the power system of the geographical islands. | Based on the required amount of flexibility the SO defines appropriate balancing products | Energy assets (central assets or DER) capable of providing FCR reserve are equipped with an accurate frequency meter to continuously measure frequency of the point of grid connection in real-time | The measured frequency must be sent to the local controller capable of receiving freq. measurements in real-time | An algorithm on the PLC compares the measured frequency with the target value and calculates the deviation | An accurate (central) frequency meter located in a major substation (e.g., Longoni, Badamiers) measures frequency of the grid in real-time | The measured frequency is received by the AGC embedded in the SCADA. | The frequency measurements need to be persisted and available in real time and for later analysis. The SCADA (where AGC is embedded) saved the measurements in a database. | Calculate the difference between the current measured frequency and the define nominal (target) frequency (e.g., 50 Hz) | Based on the actual frequency deviation and its change in time the control algorithm calculates the new FRR setpoint | The SO publishes the document describing the balancing services, their technical and administrative requirements and tendered products. | (3rd party) flexibility providers able to fulfil the SO’s requirements prepare for participation via the FMTP, directly or by aggregation via an intermediate platform (e.g., analyse available flexible power, identify suitable flexibility services and products, fulfil technical requirements). Finally, the flexibility provider or aggregator requests the prequalification of the DER (if directly connected to the FMTP). | Aggregators prepare for balancing service provision, implementing the technical requirements and establishing contracts with flexibility providers. Finally, the aggregator requests the prequalification of the intermediate platform. | The SO and flexibility provider (and aggregator if involved) conduct a series of tests to confirm the technical and administrative capability of the DER (and intermediate platform if involved) to provide the balancing services according to the SO’s requirements. The step is finalized by issuing the confirmation of prequalification by the SO. | The SO details the balancing market products and starts a tendering process and informs all prequalified flexibility providers about the tender | The prequalified flexibility providers forecast the available power for the tendered balancing service products and calculate the costs of service provision. Then the most suitable balancing products are identified and balancing service bids are submitted via FMTP. | The SO selects the most favourable bids for flexibility service provision according to the tendering rules and informs the flexibility providers about acceptance or rejection of their bids via the FMTP. The acceptance of a balancing service bid is equivalent to a legal contract between SO and flexibility provider. | The FCR functionality is unlocked via the PLC of the DER during the timespan defined in the accepted FCR bid. | The PLC calculates the FCR setpoint depending on the frequency deviation (calculated on-site and in real time, see scenario 2) based on an algorithm defined by the SO; e.g., a linear curve PFCR=f(Df) | The DER adapts the active power feed-in (or consumption) according to the FCR setpoint within the required FAT. | As long as the FCR service provision is enabled (timespan of the accepted FCR bid), the PLC sends monitoring data to the FMTP, where it is forwarded to the AGC) | The AGC receives the FCR monitoring data and compares the measurements with the expected behaviour. | The SO informs the flexibility provider about the FCR malperformance and orders immediate correction of the behaviour | The flexibility provider updates the DER control algorithms in order to remedy the FCR malperformance and to provide the FCR service according to technical specifications. | The FRR functionality is unlocked on the intermediate platform and/or the PLC of the DER during the timespan defined in the accepted FRR bid. The PLC starts waiting to receive activation requests from the FMTP or intermediate platform. | The new FRR setpoint is dispatched between central balancing assets (diesel engines operated by the SO) and distributed balancing assets (DER operated by third party). | Central balancing assets (operated by the SO) receive their new individual setpoint | The updated FRR setpoint is received by the FMTP platform. | The FMTP distributes the received FRR setpoint between the contracted flexibility providers (DERs or intermediate platforms) based on predefined rules (pro-rata or according to merit order), and submits the activation requests (direct setpoint or activation schedule). | The intermediate platform disaggregates the received activation request and forwards the setpoints to the connected DER, which previously indicated availability. | The DER changes its generation or consumption according to the received setpoint within the required FAT (details see scenario 8). | As long as the FRR service provision is enabled (timespan of the accepted FRR bid), the DER sends monitoring data to the intermediate platform. | The intermediate platform receives monitoring data from the connected DER and aggregates the values. The aggregated values are sent to the FMTP. Alternatively, large DER send monitoring data directly to the FMTP, without aggregation via an intermediate platform. | The FMTP receives the FRR monitoring data and compares the measurements with the expected behaviour. | In case of doubts, the SO compares FRR monitoring data with (public) meter readings. | The SO informs the flexibility provider about the FRR malperformance and orders immediate correction of the behaviour. | The flexibility provider updates the DER control algorithms in order to remedy the FRR malperformance and to provide the FRR service according to technical specifications. | In the morning hours the energy activated during the previous day is calculated individually for each balancing service contract (accepted bid). | The activated energy and reserved capacity (provided by the aggregator or flexibility provider) is accounted per accepted bid and summarized by flexibility provider. | The daily remuneration of balancing service provision is summarized for the entire past month and remunerated to each flexibility provider | The flexibility provider forecasts the amount and costs of the balancing service provision for the next tender period. | The aggregator receives the flexible capacity & cost forecasts of all contracted flexibility providers (DERs) and creates a merit order of flexibility. | The aggregator participates in the balancing service tender, creates bids and submits the bids to the FMTP. (See scenario 4) | The aggregator informs the connected DER about required flexibility reservation for the next product period and the conditions for balancing service provision. | The DER reserves the requested flexibility for the product period. | The DER calculates the actual flexibility bandwidth in real time and reports the values to the intermediary platform. | The PLC receives a setpoint to start an activation | After receiving a new setpoint (see (see scenario 6), the PLC of the DER initiates the activation program (ramp-up) in order to meet the setpoint received from the intermediary platform within the FAT. | The PLC receives a new setpoint to change the power of an activation | The PLC of the DER updates the activation program (ramp-up) in order to meet the new setpoint within the FAT. | The PLC receives a setpoint of 0 MW to end the ongoing activation. | The PLC of the DER initiates the end activation program (ramp-down) in order and the balancing energy provision within the FAT. | The DER processes the actual measurements and sends the required monitoring data to the intermediary platform.
| Service | CREATE | GET | CREATE | CREATE | CREATE | CREATE | CREATE | GET | CREATE | CREATE | GET | REPORT | CREATE | CHANGE | CREATE | EXECUTE | EXECUTE | EXECUTE | CREATE | CREATE | EXECUTE | CREATE | CREATE | EXECUTE | CREATE | CREATE | REPORT | EXECUTE | CREATE | CREATE | GET | GET | EXECUTE | EXECUTE | EXECUTE | CREATE | CREATE | CREATE | EXECUTE | REPORT | EXECUTE | EXECUTE | CREATE | EXECUTE | CREATE | CREATE | CREATE | CREATE | EXECUTE | CREATE | GET | EXECUTE | GET | EXECUTE | GET | EXECUTE | CREATE
| Information producer (actor) | SO | SO | SO | SO | SO | SO | Frequency meter | Frequency meter | PLC | Frequency meter | Frequency meter | SCADA | AGC | AGC | SO | Flexibility providers | Aggregator | SO | SO | Flexibility provider or aggregator | SO | PLC | PLC | DER | PLC (DER) | AGC | SO | Flexibility providers | Intermediate platform, PLC | AGC | Central balancing asset (diesel engines) | FMTP | FMTP | Intermediate platforms | DER | PLC (DER) | Intermediate platform | FMTP | SO | SO | Flexibility provider | SO | SO | SO | Flexibility provider (DER) | Aggregator (intermediary platform) | Aggregator | Aggregator | Aggregator | PLC (DER) | Intermediary platform | PLC (DER) | Intermediary platform | PLC (DER) | Intermediary platform | PLC (DER) | PLC (DER)
| Information receiver (actor) | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | /
| Information exchanged (IDs) | IE-01-01 (frequency bandwigth and emergency thresholds) | IE-01-02 (system model) IE-01-03 (historic measurements) IE-01-04 (fault statistics) | IE-01-05 (mid-term & long-term forecasts) | IE-01-06 (design scenarios) | IE-01-07 (required amount of balancing reserve) | IE-01-08 (definition of balancing products and requirements) | IE-02-01 (Network frequency) | IE-02-01 (Network frequency) | IE-02-02 (frequency deviation) | IE-03-01 (grid frequency) | IE-03-01 (grid frequency) | IE-03-01 (grid frequency) | IE-03-02 (frequency deviation) | IE-03-03 (updated FRR setpoint) | IE-04-01 (balancing services rules) | IE-04-02 (Request for prequalification of DER) | IE-04-03 (Request for prequalification of platform) | IE-04-04 (confirmation of prequalification) | IE-04-05 (rules and schedules of balancing service tender) | IE-04-06 (balancing service bid document) | IE-04-07 (balancing service bid acceptance) | IE-05-01 (FCR provision enabled) | IE-05-02 (FCR setpoint) | IE-05-02 (FCR setpoint) | IE-05-03 (FCR monitoring data) | IE-05-04 (FCR validation report) | IE-05-04 (FCR validation report) | IE-05-04 (FCR validation report) | IE-06-01 (FRR provision enabled) | IE-06-02 (setpoints for central balancing assets) IE-06-03 (setpoint for DER) | IE-06-02 (setpoints for central balancing assets) | IE-06-03 (setpoint for DER) | IE-06-04 (activation requests) | IE-06-05 (individual setpoints) | IE-06-05 (individual setpoints) | IE-06-06 (individual FRR moni-toring data) | IE-06-07 (aggregated FRR monitoring data) | IE-06-08 (FRR validation report) | IE-06-08 (FRR validation report) | IE-06-08 (FRR validation report) | IE-06-08 (FRR validation report) | IE-04-07 (balancing service bid acceptance) IE-06-07 (monitoring data) | IE-07-01 (daily balancing service accounting) | IE-07-02 (monthly balancing service accounting and remuneration report) | IE-08-01 (forecast of flexible capacity and costs) | IE-08-02 (flexibility merit order) | IE-04-06 (balancing service bid document) | IE-08-02 (Flexibility reservation request) | IE-08-02 (Flexibility reservation request) | IE-08-03 (actual flexibility of DER) | IE-06-05 (individual setpoints) | IE-06-05 (individual setpoints) | IE-06-05 (individual setpoints) | IE-06-05 (individual setpoints) | IE-06-05 (individual setpoints) | IE-06-05 (individual setpoints) | IE-06-06 (individual FRR monitoring data)
| Reference to Scenario number | R-01-01 (guidelines for operation defined by regulator) | R-01-02 (historic data about electricity system, load and frequency) | R-01-03 (List of planned new DER installations) | IE-01, IE-02, IE-03, IE-04, IE-05 received | IE-01, IE-02, IE-03, IE-04, IE-05, IE-06 received | IE-01-07 received | R-02-01 (frequency meter on-site) | R-02-02 (on-site PLC) | R-02-01 (frequency meter on-site) | R-03-01 (central frequency meter) | R-03-02 (AGC) | R-03-03 (data storage) | R-03-02 (AGC) | R-03-04 (P-f- control algorithm) | IE-01-08 | IE-04-01 available | IE-04-01 available | IE-04-02 or IE-04-03 available | IE-01-08 | IE-04-05, R-04-01 (prequalified flexibility providers) | IE-04-06 received | IE-04-07 (accepted FCR bid) | IE-02-02 (frequency deviation) R-05-01 (P(Df) characteristics implemented) | R-05-02 (DER operative) | R-05-03 (communication. channel between PLC and FMTP) R-05-05 (active power meter (on-site)) | R-05-04 (algorithm to validate FCR performance) |  |  | IE-04-07 (accepted FRR bid) | R-06-01 (dispatching algorithm) | R-06-02 (central balancing asset available) | R-06-03 (FMTP available) R-06-07 (comm. channel between AGC and FMTP) | R-06-03 (FMTP available) R-06-06 (communication channel between FMTP and intermediate platforms or large DER) | R-06-04 (DER available) R-06-05 (communication channel between DER and intermediate platform) | R-06-04 (DER available) | R-06-05 (communication channel between DER and intermediate platform) R-05-05 (active power meter, on-site) | R-06-06 (communication channel between FMTP and intermediate platforms or large DER) | R-06-08 (algorithm to validate FRR performance) | R-06-09 (meter data) |  |  | IE-06-08 (FRR validation report) IE-05-04 (FCR validation report) | IE-04-07 (balancing service bid acceptance) | IE-07-01 (daily balancing service accounting) | R-08-01 (Operational forecast of DER) | IE-08-01 R-06-05 (communication channel between DER and intermediate platform) |  | R-06-05 (communication channel between DER and intermediate platform) |  | R-06-05 (communication channel between DER and intermediate platform) | [6 empty] | R-05-05 (active power meter (on-site))
5 Information exchanged
Requirement, R-Ids
| Information exchanged, ID | IE-01-01 | IE-01-02 | IE-01-03 | IE-01-04 | IE-01-05 | IE-01-06 | IE-01-07 | IE-01-08 | IE-02-01 | IE-02-02 | IE-03-01 | IE-03-02 | IE-03-03 | IE-04-01 | IE-04-02 | IE-04-03 | IE-04-04 | IE-04-05 | IE-04-06 | IE-04-07 | IE-05-01 | IE-05-02 | IE-05-03 | IE-05-04 | IE-06-01 | IE-06-02 | IE-06-03 | IE-06-04 | IE-06-05 | IE-06-06 | IE-06-07 | IE-07-01 | IE-07-02 | IE-08-01 | IE-08-02 | IE-08-03
| Name of information | frequency band-width and emergency thresholds | System model | historic measurements | Fault statistics | Consumption forecasts | Design scenarios | Required amount of balancing reserve | Balancing products and requirements | Network frequency | Frequency deviation | Grid Frequency | Frequency deviation | Updated FRR setpoint | Balancing services rules | Request for prequalification of DER | Request for prequalification of platform | Confirmation of prequalification | Rules and schedules of balancing service tender | Balancing service bid document | Balancing service bid acceptance | FCR provision enabled | FCR setpoint | FCR monitoring data | FCR validation report | FRR provision enabled | FRR setpoints for central balancing assets | FRR setpoint for DER | FRR Activation requests | Individual FRR setpoints | Individual FRR monitoring data | Aggregated FRR monitoring data | Daily balancing service accounting | Monthly balancing service accounting and remuneration report | Forecast of flexible capacity and costs | Flexibility merit order | Actual flexibility of DER
| Description of information exchanged | Predefined bandwidth of allowed system frequency, including target value (50 Hz) and thresholds for initiating emergency measures | Model of the power system supporting dynamic analyses | Historic timeseries of measured generation, consumption and system frequency | Statistics of faults in the power system that are relevant for balancing reserve dimensioning | Mid-term (timeseries) of the total consumption | Expected critical situations (e.g., yearly peak load, separation of parts of the grid, etc.) relevant for balancing reserve dimensioning | Required number of balancing reserves to ensure a stable operation of the power system, (e.g., 99.975% reliability) | Definition of balancing products and requirements comprising: products (duration, min. bid size, direction, tolerances) | Actual measurements of network frequency measured on-site by DER | Actual frequency deviation detected on-site at DER | Actual measurements of grid frequency centrally acquired by SO | Actual frequency deviation detected centrally by SO | Actual FRR setpoint calculated by AGC, sum for all assets participating in FRR service provision | The document describing the rules for participation in balancing services, their technical and administrative requirements and tendered products, as well as the prequalification procedure | The flexibility provider (DER operator) applies for the prequalification for the balancing service participation. | The aggregator (intermediate platform operator) applies for the prequalification for the balancing service participation. | The SO confirms the successful prequalification of a DER or platform. Confirmation may need to be renewed after an expiry period. | The SO publishes the rules and schedules of balancing service tender, including description of tendered balancing service products. | The aggregator or flexibility provider participates in the tender for balancing services by submitting one or multiple binding bids. Bids contains ID of bidder, date, timespan, product ID, power, capacity price, energy price. | The SO informs the bidders about acceptance or rejection of the bids submitted in the tender. | The (PLC of the) DER enabled the FCR functionality and starts detecting the frequency deviations. | FCR setpoint calculated on-site by PLC (DER) | The FCR monitoring data includes local measurements of frequency, active power, calculated setpoint, actual FCR provision. It is submitted in short intervals (e.g., of 2s). | The FCR validation report summarizes the quality of FCR service provision of a flexibility provider. | The (PLC of the) DER enabled the FCR functionality and starts listening for incoming setpoints | FRR setpoints for central balancing assets (controlled by the SO) | FRR setpoints for DER (controlled by 3rd party flexibility providers) |  | Individual FRR setpoints for DER controlled via an intermedia platform | Monitoring data of individual DER, which is sent to an intermediate platform Datapoints: active power, baseline, setpoint, FRR activation, control bandwidth | Aggregated monitoring data of a pool of DER (managed by an intermediary platform), which is sent to the FMTP. Datapoints: active power, baseline, setpoint, FRR activation, control bandwidth | Accounting of provided balancing energy and related costs (according to balancing service bid document), created on d+1 | Monthly sum of Daily balancing service accounting positions, which are used for remuneration of the flexibility provider | The forecast of flexible capacity and costs of a DER is generated for the entire upcoming product duration, that is tendered. | The flexibility merit order sorts the DER’s flexibility forecasts according to their costs (from cheapest to most expensive). | The actual flexibility bandwidth of a DER
Note on B5: Lucas Pons Bayarri: Use cases can be used in various areas (e.g. energy system). Within these areas, different domains are used to define/determine a more specific subgrouping. Zones might describe additional zones with an automation system or a reference architecture (SGAM). Experts in a particular field could suggest their set of domain (and zones) in order to provide a common understanding how to group use cases within a complex area. These predefined domains (and zones) can be chosen by the author of the use case (preselection). The author can select one or more domains and zone, comma separated, as it is usual that use cases are crossing different domains and zones. Example domains: Generation, transmission, DER, distribution, customer premises. Example zones: Process, field, station, operation, enterprise, market
Note on B7: Lucas Pons Bayarri: Insert one column per version. Do not remove previous columns in order to keep track of past versions. These set of field will be expanded in columns on any new version
Note on B10: Lucas Pons Bayarri: Comma-separated list
Note on B12: Lucas Pons Bayarri: will be used within the standardization organizations. The procedures for validation of use cases or actors will be defined in part 1 of this standard. EXAMPLE Similar to working draft, committee draft (CD) for comments, committee draft for vote (CDV), for voting (similar FDIS), final
Note on B16: Lucas Pons Bayarri: Comma separated list of related use cases
Note on B20: Lucas Pons Bayarri: Insert one column per KPI. This set of columns will expand in columns on any addtional KPI
Note on B25: Lucas Pons Bayarri: Insert as much assumptions and prerequisites as needed in columns. This set of rows will be expanded in columns
Note on B29: Lucas Pons Bayarri: Known relations to other use cases can be provided here if e.g. the use case is a more detailed one related to a high level use case, or it is an alternative to an existing use case. The type of relation like “include”, “extends”, “invokes” might be used in order to specify this relation in more detail.
Note on B30: Lucas Pons Bayarri: Use cases can be described on different levels (refer to IEC62559-1 for examples). Currently there is no fixed hierarchy for use cases defined, but some most common examples are provided. EXAMPLE High level use case, generic use case, specialised use cases.
Note on B31: Lucas Pons Bayarri: EXAMPLE: Obligatory/mandatory, optional, nice to have.
Note on B32: Lucas Pons Bayarri: On international level, the use case description might be generic enough to describe a use case in a more general way independently from the national or regional market design. But use cases might be used to describe regional or national specific circumstances like laws or even project-specific details. If the use case reflects those circumstances, it should be characterized accordingly. EXAMPLE National, "Country".
Note on B33: Lucas Pons Bayarri: This field can help to classify the main focus of the use case. EXAMPLE Technical/system use case, business use cases (e.g. market processes), political, test use cases.
Note on B35: Lucas Pons Bayarri: Insert one row per general remark of the use case. This row will be expanded by columns
Note on B36: Lucas Pons Bayarri: for further comments which are not considered elsewhere.
Note on B37: Lucas Pons Bayarri: Insert one column per diagram associated to this use case. This set of rows will be expanded by columns. Each diagram should be later uploaded to the github along with this template filled up. The name of the diagram files uploaded must match thr name specified in this section
Note on B39: Lucas Pons Bayarri: Activity, component, functional, sequence, etc..
Note on B40: Lucas Pons Bayarri: image or URL
Note on B41: Lucas Pons Bayarri: Insert the name of the diagram exactly like the one that will be uploaded
Note on B43: Lucas Pons Bayarri: Insert one column per actor. These set of rows will be expanded by columns. The concept of an “actor” is very general and can cover: People (their roles or jobs), systems, databases, organizations, and devices involved in or affected by the use case: e.g. operators, system administrators, technicians, end users, service personnel, executives, SCADA system, real-time database, regional transmission operator (RTO), remote terminal units (RTU), intelligent electronic devices (IED) and even the power system. It is recommended to use actors as described in the ENTSO-E role model: https://eepublicdownloads.entsoe.eu/clean-documents/EDI/Library/HRM/Harmonised_Role_Model_2020-01.pdf
Note on B44: Lucas Pons Bayarri: The actor list can be grouped in order to provide a better overview. Naming convention: For complex groupings, the group name can be “dot-delimited”. EXAMPLE (area.domain.) main.sub.subsub. The grouping may follow the suggested domains/zones previous section
Note on B45: Lucas Pons Bayarri: Brief description of the group
Note on B46: Lucas Pons Bayarri: Actor name according to an existing taxonomy OR actor name especifically defined for this project
Note on B47: Lucas Pons Bayarri: If the actor is already defined in an existing and well-know actors taxonomy, just add here the name of the taxonomy (EXAMPLE: ENTSO-E role model). If not, here the type of actor should be provided
Note on B48: Lucas Pons Bayarri: In case the actor is not described in any existing taxonomy, the description mandatory. If the actor is already described ina taxonomy and the taxonomy is specified in the previos field, this field is not required
Note on B50: Lucas Pons Bayarri: Insert one column per reference. These set of rows will be expanded by columns.
Note on B53: Lucas Pons Bayarri: There are different reference types as shown in the examples above (e.g. standards, regulation, contract, others like publications)
Note on B54: Lucas Pons Bayarri: Any references shall be identified that might restrict or affect the design, understanding, and requirements of the use case, including contracts, regulations, policies, financial considerations, engineering constraints, pollution constraints, and other environmental quality issues
Note on B55: Lucas Pons Bayarri: e.g. NP, CD, CDV, FDIS, IS
Note on B56: Lucas Pons Bayarri: Where does the document influence the use case? e.g. copy right, IPR
Note on B57: Lucas Pons Bayarri: Who published the document?
Note on B58: Lucas Pons Bayarri: If available, a public link can be provided (e.g. to the IEC webstore for standards).
Note on B60: Lucas Pons Bayarri: Focuses on describing scenarios of the use case with a step-step analysis (sequence description).
Note on B61: Lucas Pons Bayarri: Insert one column per condition. These set of rows will be expanded by columns
Note on B65: Lucas Pons Bayarri: describes which actor(s) trigger(s) this scenario.
Note on B66: Lucas Pons Bayarri: describes which event(s) trigger(s) this scenario.
Note on B67: Lucas Pons Bayarri: Describes which condition(s) should have been met before this scenario happens.
Note on B68: Lucas Pons Bayarri: describes which condition(s) should prevail after this scenario happens The post conditions may also define “success” or “failure” conditions for each use case.
Note on B69: Lucas Pons Bayarri: Insert one column per step. These set of rows will be expanded by columns. For the scenario, all the steps performed shall be described going from start to end using simple verbs like – get, put, cancel, subscribe etc. Steps shall be numbered sequentially – 1, 2, 3 and so on. Should the scenario require detailed descriptions of steps that are also used by other use cases, it should be considered creating a new “sub” use case, then referring to that “subroutine” in this scenario.
Note on B70: Lucas Pons Bayarri: Refers to the name of one of the scenarios defined in the previous section
Note on B72: Lucas Pons Bayarri: The event that triggers the step. This might be completion of the previous step. EXAMPLE A human requesting the function, data being reported periodically, or a power system event
Note on B73: Lucas Pons Bayarri: Label that would appear in a process diagram. Action verbs should be used when naming activity.
Note on B74: Lucas Pons Bayarri: This describes what action takes place in this step. The focus should be less on the algorithms of the applications and more on the interactions and information flows between actors.
Note on B75: Lucas Pons Bayarri: This column identifies the nature of the information flow and the originator of the information. Available options are CREATE, GET, CHANGE, DELETE, CANCEL, EXECUTE derived from IEC 61968-100:2013, 6.2.2. Additionally, REPORT, TIMER and REPEAT are suggested. CREATE means that an information object is to be created at the Producer. GET (this is the default value if none is populated) means that the Receiver requests information from the Producer (default). CHANGE means that information is to be updated. Producer updates the Receiver’s information. DELETE means that information is to be deleted. Producer deletes information from the Receiver. CANCEL, CLOSE imply actions related to processes, such as the closure of a work order or the cancellation of a control request. EXECUTE is used when a complex transaction is being conveyed using a service, which potentially contains more than one verb. REPORT is used to represent transferral of unsolicited information or asynchronous information flows. Producer provides information to the Receiver. TIMER is used to represent a waiting period. When using the TIMER service, the Information Producer and Information Receiver fields shall refer to the same actor. REPEAT is used to indicate that a series of steps is repeated until a condition or trigger event. The condition is specified as the text in the “Event” column for this row or step. Following the word REPEAT, shall appear, in parenthesis, the first and last step numbers of the series to be repeated in the following form REPEAT(X-Y) where X is the first step and Y is the last step. These common service definitions are related to automation/information or communication systems. In case the use case template is applied in other domains, further services might be used and described.
Note on B76: Lucas Pons Bayarri: This identifies the producer or source of the information. This should be one of the actors in the reference template section.
Note on B77: Lucas Pons Bayarri: This identifies the receiver of the information. This should also be one of the actors identified above
Note on B78: Lucas Pons Bayarri: This describes briefly the information to be exchanged between the two actors – information producer and information receiver: – Input to the use case from some external sources that is not described in this use case. – Internal to the use case (e.g. between different applications and systems within the use case). – Output from the use case that will be used by other actors/entities not included in this use case. – This column should not contain technology issues/requirements. – It is allowed to list several information in one step, comma separated. – Summarizing the information exchanged between two actors based on the relevant set of use cases can characterize the needed communication/message payload. – Detailed information exchange should be identified using an ID (“Name of Information”). Such name should include the source namespace, if not referring to the by-default one. In this case, the column only contains the ID of the exchanged information which link to more details about the information in a separate table in the following template section 5 which is used for all steps of the use case. Here the information can use a short ID referring to template section 5 for further details. Several information exchanged IDs can be listed, comma separated.
Note on B79: Lucas Pons Bayarri: Refers to the Number of one of the scenarios defined in the previous section
Note on B80: Lucas Pons Bayarri: Insert one column per information item. These set of rows will be expanded by columns.
Note on B81: Lucas Pons Bayarri: the requirement id Can be used to define requirements referring to the information and not to the step as in the step by step analysis (see template section 6 below): EXAMPLE Data protection class corresponding to this information object.
Note on B82: Lucas Pons Bayarri: Unique ID which identifies the selected information in the context of the use case.
Note on B83: Lucas Pons Bayarri: Unique ID which identifies the selected information in the context of the use case.
Note on B84: Lucas Pons Bayarri: Brief description, in case a reference to existing data models/information classes should be added. Using existing canonical data models is recommended.

## Instructions
Mandatory: All the cells in Column C in yellow have to be completed mandatorily.
Optional: The cells in blue are for multiple objects, that can be completed when needed.