## IEC62559-2
1 Description of the use case
1.1 Name of use case
Use case identification
| ID | SOCL-CY-02
| Area/ Domain(s)/ Zone(s) | Country market layer
| Name of use case | Reactive power flexibility and power quality
1.2 Version management
| Version No. | 4
| Date | 2021-08-03
| Name of author(s) | Markos Asprou, Lenos Hadjidemetriou
Changes
Approval status
1.3 Scope and objectives of use case
| Scope | Enhance of reactive power flexibility and power quality (i.e., voltage support, congestion management, phase balancing) through the use of distributed flexible resources (energy storage and PV systems)
| Objective(s) | • Maintain voltage stability • Demonstrate congestion management for maintaining capacity limits of the grid • Achieve power quality enhancement
Related business case(s)
1.4 Narrative of use case
| Short description | Cyprus power system favors the massive installation of PV due to the climate conditions (abundant of sun) in order to achieve the national environmental target. The high penetration of renewables in specific feeders causes local congestion problems (voltage and thermal limit violations) in the distribution grid. In addition, the majority of loads are single phase connected to the grid, creating intense phase imbalances and thus the power quality and the grid capacity are negatively affected. Reactive power flexibilities provided within this use case will enhance the voltage stability, relieve the congestion of the system and increase the system efficiency, while phase balancing services will improve the power quality and increase the system capacity by symmetrizing the phase loading. Therefore, this business use case exploits the flexible resources of the distribution grid (large energy storage systems, PV parks, prosumers) to provide reactive power and phase balancing services. These services will be procured by the distribution system operator (DSO) to the DSO local market. The information exchange between the DSO control center and the local DSO market will be facilitated by the OneNet system. The energy market will allocate the services to the different flexible actors (aggregators and prosumers) according to the market rules. The activation of these services will be coordinated by the operators and/or based on the grid operating conditions. Currently, the reactive/voltage support is performed by reactors/capacitors installed in the transmission level or by predefined support schemes (i.e., cosφ(P)) provided by the PV inverters in the distribution grid. In addition, phase balancing has recently introduced in the IEEE standards for microgrids but has not been used in distribution grids. In this business use, reactive support and phase balancing will be provided by flexible resources and will be online coordinated by DSO to increase efficiency, relieve congestion, reduce curtailments and increase PV penetration. The flexible resources will be remunerated for these services enhancing their competitiveness in the energy market.
| Complete description | The DSO monitors the system in real time to ensure the proper operation of the system within the desired limits. The monitoring of the distribution grid is enabled by smart meter and SCADA. In this BUC the Active Balancing congestion management platform at the DSO control center (ABCM-D) play a critical role, while the OneNet system facilitates the information exchange between the different actors in the distribution grid. A high-level description for the congestion management is provided below: • The DSO procures congestion management products (phase balancing and reactive support) to the DSO local market. • The DSO sends the location-based prequalified operational limits (as they were calculated through the ABCM-D platform) to the DSO local market in order to ensure the safe operation of the distribution grid. • FSPs at the distribution level send their activation bids in the local DSO market • The local DSO market is cleared and the awarded activation bids are sent to the qualified FSPs at the distribution level. • In the occurrence of a power quality issue or voltage limit violation the awarded FSPs are activated through coordination signals sent by the ABCM-D platform in order to overcome grid congestion. • The DSO through the ABCM-D platform evaluate the response of their FSPs to the congestion management event and send an evaluation report to the DSO local market.
1.5 Key performance indicators (KPI)
ID
| Name | Voltage limits violations | Energy losses | Loading asymmetries | Overloading
| Description | This indicator will provide information for the duration and the intensity of the over/under-voltage conditions occurs at the distribution grid | Energy losses dissipated to the distribution grid | This indicator will provide information about the loading asymmetry of the three phases, before and after the power quality enhancement | This indicator will provide information for the duration and the intensity of the overloading conditions occurs at the distribution grid
| Reference to mentioned use case objectives | Congestion management, Voltage stability | Congestion management | Power quality enhancement | Congestion management
1.6 Use case conditions
| Assumptions | The use case will be developed and demonstrated in a non-invasive environment using the real time digital twin of the Cyprus power system. | The TSO, DSO control center and the energy market will be emulated in the demo architecture. | The energy market will be based on a generic market setup in the absence of an energy market in Cyprus. | Additional PVs and energy storage systems will be installed to represent near future conditions. | Aggregators and prosumers will be emulated in the demonstration considering online coordination capabilities by system operators.
| Prerequisites | Provision of PMU data from the transmission system | Provision of SCADA data and/or smart meter data from the distribution grid | Adoption of a generic energy market setup.
1.7 Further information to the use case for classification/mapping
Relation to other use cases
Level of depth
Prioritisation
| Generic, regional or national relation | Regional and national
| Nature of the use case | BUC
| Further keywords for classification | Reactive power, flexibility, voltage stability, congestion, power quality
1.8 General remarks
General remarks
2 Diagrams of use case
Diagram name
Diagram type
| Diagram URI type | SOCL-CY-02_use_case_overview | SOCL-CY-02_scenario1_activities
Diagram URI value
3 Technical details
3.1 Actors
Grouping
Group description
| Actor name | Transmission system Operator | Distribution system operator | Aggregator | Prosumer | Market operator | Flexibility Service Provider (FSP)
| Actor type | Business | Business | Business | Business | Business | Business
| Actor description | A party responsible for operating, ensuring the maintenance of and, if necessary, developing the system in a given area and, where applicable, its interconnections with other systems, and for ensuring the long-term ability of the transmission grid to meet reasonable demands for the transmission of electricity. | A party responsible for operating, ensuring the maintenance of and, if necessary, developing the system in a given area and, for ensuring the long-term ability of the distribution grid to meet reasonable demands for the distribution of electricity. | A party that aggregates resources for usage by a service provider for energy market services. | A party that produces and consumes electricity. | A market operator is a party that provides a service whereby the offers to sell electricity or electricity flexibility are matched with bids to buy electricity or electricity flexibility. | A party providing flexibility services to energy stakeholders via bilateral agreements or flexibility markets.
Further information specific to this use case
3.2 References
Name
No.
References type
Reference
Status
Impact on use case
Originator/organisation
Link
4 Step by step analysis of use case | 4.1 Overview of scenarios
Scenario conditions
| No. | 1
| Scenario name | Reactive power compensation and power quality enhancement
| Scenario description | Monitoring and evaluation of the distribution grid operating conditions by the DSO. In case of voltage or power factor limit violation the DSO will coordinate the flexible resources to provide reactive power flexibility and power quality services (phase balancing). The flexible resources participating in this scenario have already been awarded by the market (declaring their availability through bids) and their bids have been pre-qualified by the DSO in order to participate to the reactive power compensation and power quality enhancement.
| Primary actor | FSP (energy storage, PVs) Aggregators Prosumers DSO
| Triggering event | Measured operating condition in distribution feeder
| Pre-condition | Sensor and smart meters are connected with the SCADA and AMI system to measure in real time the distribution grid operating conditions.
| Postcondition | Flexible resources will regulate the provision of reactive power flexibility and power quality services to relieve the congestion in the distribution grid, and improve the grid efficiency and power quality.
4.2 Steps – Scenarios
| Scenario name: | Reactive power compensation and power quality enhancement | Reactive power compensation and power quality enhancement | Reactive power compensation and power quality enhancement | Reactive power compensation and power quality enhancement | Reactive power compensation and power quality enhancement | Reactive power compensation and power quality enhancement | Reactive power compensation and power quality enhancement | Reactive power compensation and power quality enhancement
| Step No. | 1.1 | 1.2 | 1.3 | 1.4 | 1.5 | 1.6 | 1.7 | 1.8
| Event | Products procurement for frequency balancing | Prequalification of location-based limits | Bidding to the local DSO for the frequency products | Awarded bids are sent to the FSPs | Observe congestion to the distribution grid (power quality and power factor issues) | Decision making to relieve congestion | Provision of congestion management services | FSPs evaluation response
| Name of process/activity | Procurement of Products | Prequalification | Bidding | Market clearing | Monitoring the distribution grid | Coordination of available flexible resources | Improvement of power quality and power factor | Online evaluation of the congestion management process and the response of the FSPs to the event
| Description of process/activity | DSO sends procured products to the DSO local market through the OneNet System | DSO determines the admissible limits (for having a safe operation of the grid) at the MV/LV interface. This is done through using ABCM-D. The limits are sent to local DSO market through the OneNet system. | FSPs in the distribution level bid for the congestion management procured products in the market through the OneNet system. | DSO local market are cleared, and the awarded bids are sent through the OneNet system to the FSPs | Measurements from distribution substations are received by the DSO SCADA. Measurements from smart meters are received by the DSO AMI. The ABCM-D platform will process the measurement based on monitoring schemes and alarms will be provided in case of power quality or power factor limit violation. | Based on the location of the congestion (power quality and power factor limit violation) the DSO defines the coordination set-points for the activation of the flexible resources through the ABCM-D platform. The coordination signals are sent to the flexible resources through the OneNet system | The flexible resources increase or decrease the reactive power output to provide phase balancing and power factor correction services according to the DSO coordination set points in order to relieve the congestion. | DSO monitor the flexible resources based on smart meters for evaluating their responsiveness to the requested product. The evaluation report is provided to the market.
| Service | CREATE | EXECUTE | CREATE | EXECUTE | REPORT | CREATE | EXECUTE | REPORT
| Information producer (actor) | DSO | DSO | FSPs | DSO local market | SCADA, smart meters | DSO | FSP, Aggregator, Prosumer | DSO
| Information receiver (actor) | DSO local market | DSO local market | DSO local market | FSP | DSO | FSP, Aggregator, Prosumer | DSO | Market operator
| Information exchanged (IDs) | I1-01 | I1-02 | I1-03 | I1-04 | I1-05 | I1-06 | I1-07 | I1-08
Reference to Scenario number | bar: I1-01
5 Information exchanged | Requirement, R-Ids | bar: I1-01
| Information exchanged, ID | I1-01 | I1-02 | I1-03 | I1-04 | I1-05 | I1-06 | I1-07 | I1-08
| Name of information | Procured products | Prequalified limits | Bids of the FSPs | Awarded bids | Measurements | Coordination signals | Measurements | Report
| Description of information exchanged | DSO procures products for congestion management services | DSO send to market the location based prequalified limits that should be respected. | FSPs send bids for the congestion management products to the market | Market sends the awarded bids to the qualified FSPs in the distribution level | Measurements from smart meters are reported to the DSO AMI | Coordination signals are sent to the flexible resources by the DSO. | Smart meters and SCADA measurements are used for evaluating the response of FSPs during the congestion management event | DSO report to the market operator the evaluation report for the congestion management services by the flexible resources

## Instructions
Mandatory: All the cells in Column C in yellow have to be completed mandatorily.
Optional: The cells in blue are for multiple objects, that can be completed when needed.